## Sheet1
Augustana Lutheran | 2023-11-01
Chiller Evaluation
Manufacturer | Model | Tonnage | Compressor Type | Refrigerant | # of Condenser Fans | Chilled Water Flow w/30-35% glycol (gpm) | Evaporator Pressure Drop (ft H2O) | Energy Efficiency Rating -EER (BTU/Wh) | Integrated Part Load Value -IPLV (BTU/Wh) | Chiller Control | Length x Width x Height (inches) | Shipping Weight (lbs) | Warranty | Budgetary Cost ($) | Delivery Time (weeks) | Sales Engineer, Company
Carrier | 30XV140 | 129 | VFD Screw | R-513A | 10 | 309.6 | 27.2 | 10.67 | 19.97 | BACnet IP | 255 x 88 x 99 | 12353 | 1st year - parts only, Compressor 2-5 years parts only | 200000 | 40+ | Andrew Cunnigham, Carrier
Daikin | AWV010B | 129 | VFD Screw | R-513A | 10 | 367* | 5.8 | 9.73 | 16.26 | BACnet, Modbus | 217 x 88 x 100 | 12736 | 1st year - entire unit parts and labor | 155500 | 42 | Bill Roan, Long & Assoc.
York | YVAA0176 | 129 | VFD Screw | R-513A | 12 | 308.8 | 11.8 | 9.812 | 17.75 | No information | 291 x 88 x 93 | 15869 | No information | 181900 | 51 | Mike Schwenk, CFM Co.
Carrier | 30RC-1525S015-D-8 | 136.6 | Standard Scroll | R-32 | 8 | 353.7 | 10.8 | 9.917 | 17.7 | BACnet IP | 199 x 88 x 99 | 6299 | 1st year - parts only, Compressor 2-5 years parts only | 138000 | 35 | Andrew Cunnigham, Carrier
Trane | Ascend ACS | 129.9 | Standard Scroll | R-454B | 8 | 310.95 | 8.1 | 10.709 | 17.665 | BACnet, Modbus | 229 x 88 x 98 | 7754 | No information | 130000 | 30 | Brysen Tyler, Trane
Daikin | AGZ008F | 128.5 | Standard Scroll | R-32 | 8 | 307.4* | 9.4 | 9.668 | 14.86 | BACnet, Modbus | 170 x 88 x 99 | 7012 | 1st year - entire unit parts and labor | 90400 | 42 | Bill Roan, Long & Assoc.
York | YLAA0155SJ17XFB | 135.5 | Standard Scroll | R-454B | 8 | 341.7 | 14.4 | 9.102 | 16.98 | No information | 188 x 88 x 94 | 7198 | No information | 129800 | 55 | Mike Schwenk, CFM Co.
* Water Only
Chilled Water Pump Evaluation
Manufacturer | Model | Flow (gpm) | Head (ft of water) | Size (inches) | Efficiency @Design point | Bronze Fitted | Motor HP | Motor Speed (rpm) | Enclosure | Insulation Class | Inverter Rated | Budgetary Cost ($) | Delivery Time (weeks) | Sales Engineer, Company
Armstrong | Series 4030 | 367 | 123 | 3 x 2.5 x 8 | 69.2 | yes | 20 | 3560 | TEFC | F | yes | 6090 | 7-9 | Mike Schwenk, CFM Co.
Patterson | E2B13A-2 | 367 | 123 | 3 x 2 x 13.5 | 62.7 | yes | 20 | 1800 | TEFC | H | yes | 5400 | 8 | Bill Roan, Long & Assoc.
VFD, 230V, 3 phase, 20 HP motor estimate is $2,000.